## Sheet1
System | Component | Efficiency Measure | Description
Separate Heat and power(SHP) | Thermal Efficiency(Boiler) | EFFq=Net useful thermal output/Energy Input | Net Useful thermal energy output for the fuel consumed
| Electric Only Generation | EFFp=Power Output/Energy input | Electricity Purchased From Central Stations Via Transmission Grid
| Overall Efficiency of Separate Heat and | EFFshp=(P+Q)/(p/EFFp)+(Q/EFFt) | Sum of net power(P) and useful thermal energy output (Q) divided by
| Power(SHP) |  | the sum of fuel consumed to produce each
Combined Heat And Power | Total CHP System Efficiency | EFFferc=(P+Q/2)/F | Sum of the net power and net useful thermal ouptu divided by the total
fuel (F) consumed
| FERFC Efficiency Standard | EFFferc= (p+Q/2)/F | Developed For the Public Utilitis Regulatory Act of 1978, the FERC
methodologyattempts to recognize the quality of electrical output
relative to thermal output
Effective Electical Efficiency
| (or Fuel Utilization Efficiency, FUE) | FUE=p/(F-Q/EFFt) | Ratio of Net Power output to net fuel consummption, where net fuel
Consumption excludes the portion offuel udes for producing useful heat
output. Fuel used to produce useful heat is calculated assuming typical
boiler efficiency, usually 80 percent
| Percent Fuel Savings | S=1-f/(P/EFFp)+(Q/EFFq) | Fuel savings compared the fuel used by the CHP system to a separate
heat and power system.Positive values represent fuel savings while
negative values indicate that the CHP system is using more fuel than SHP
Key:
P= Net power output from CHP system
Q=Net useful Thermal Energy from CHP system
F=-Total fuel input to CHP
EFFp=Efficiency of displaced electric generation
EFFq= Efficieny of displaced thermal generation